| S. No. | Reference / Page No. | COMPANY Comments | CONTRACTOR Response | Status / Remarks |
| --- | --- | --- | --- | --- |
| 1 | Page 1 | EPC FOR UPGRADATION OF FACILITIES AT SE FIELD |  |  |
| 2 | Page 1 | Contract No. 4700022908 Project No. P30377 Comment Code - 2 |  |  |
| 3 | Page 1 | Document No. Transmittal No. Document Title  1 Approved – No Comments  2 Approved Subject to Incorporation of Comments |  |  |
| 4 | Page 1 | FOUNDATION LAYOUT & DETAIL DRAWING FOR NEW COMPACT SUBSTATION AT WATER TANK FARM - ASAB |  |  |
| 5 | Page 1 |  3 Revise and Resubmit  4 Rejected  5 Retained for Information |  |  |
| 6 | Page 1 | RSME-P157-PRO-1601-F-010 REV 3 Page 1 of 3 |  |  |
| 7 | Page 1 | No. COMPANY Comments CONTRACTOR Response Status / Remarks |  |  |
| 8 | Page 1 | GRID DIMENSION AND CENTRE LINE DIMENSION OF SUPPORT IS NOT MATCHING WITH VENDOR GA DRAWING TYP. GRID LINE AT THE EDGE OF STEEL COLUMN NO AT THE CENTRELINE OF COLUMN, ALL GRIDS AND DIMENSIONS SHALL BE THROUGHLY CHECKED WITH VENDOR DRAWING AND UPDATED FULLY. |  |  |
| 9 | Page 1 | Noted and the drawing is updated as per latest vendor GA |  |  |
| 10 | Page 1 | GRID NUMBER NOT MATCHING DIMENSION NOT MATCHING WITH VENDOR GA, CORRECT IT AS PER FINAL DRAWING, CHECK THE NORTH ORIENTATION WITH PSS VENDOR GA DRAWING |  |  |
| 11 | Page 1 | ` Noted and the drawing is updated as per latest vendor GA |  |  |
| 12 | Page 1 | IS ONLY THIS LIFTING SLEEVE SUFFICIENT FOR FOUNDATION LIFTING, CHECK WITH DESIGN, TRY TO PROVIDE LIFTING LUG ON FOUNDATION INSTEAD PROVIDING SLEEVE ON PEDESTAL TYP. |  |  |
| 13 | Page 1 | Noted and updated in the drawing. |  |  |
| 14 | Page 1 | WATER TABLE SHALL BE CHECKED WITH GEOTECH REPORT, ACCORDINGLY PROVIDE THE CONCRETE PROTECTION AGAINST GROUND WATER PROTECTION TYP. |  |  |
| 15 | Page 1 | As per Geotech report, no water table encountered. |  |  |
| 16 | Page 1 | 5 SHEET 1 LIFTING LUG TO BE DESIGN VERIFIED TYP. Noted and presented |  |  |
| 17 | Page 2 | RSME-P157-PRO-1601-F-010 REV 3 Page 2 of 3 |  |  |
| 18 | Page 2 | THIS DRAWING IS PRELIMINARY SUBMISSION WITH AVAILABLE INPUTS, SAME TO BE UPDATED AS PER FINAL VENDOR INPUTS WITH PROPER CHECKING AND WITHOUT ANY DRAFTING ERRORS AND HOLD POINTS TO BE UPDATED IN NEXT REVISION WITH FINAL VENDOR INPUTS. |  |  |
| 19 | Page 2 | Noted and submitted based on the latest vendor data |  |  |
| 20 | Page 2 | 7 SHEET 1 TEXT TO BE IN SAME ALIGNMENT TYP. Noted and updated |  |  |
| 21 | Page 2 | ALL THE FOUNDATION DIMENSION AND RE-BAR DETAILS, PEDESTAL HEIGHT ARE TO BE VERIFIED AND UPDATED AS PER FINAL VENDOR INPUTS AND MAT 3D DESIGN |  |  |
| 22 | Page 2 | 9 SHEET 1 BOC? Noted and corrected |  |  |
| 23 | Page 2 | PEDESTAL AND FOUNDATION ORIENTATION SHALL BE AS PER FOUNDATION PLAN TYP. |  |  |
| 24 | Page 2 | 11 SHEET 1 CORRECT THE LEADERS OF FILLS TYP. Noted and updated |  |  |
| 25 | Page 3 | RSME-P157-PRO-1601-F-010 REV 3 Page 3 of 3 |  |  |
| 26 | Page 3 | CHECK THE ANCHOR BOLT SCOPE OF SUPPLY PROVIDE THE ANCHOR BOLT DETAILS, SHOW AS PER ACTUAL ANCHOR BOLT LENGTH TYP. |  |  |
| 27 | Page 3 | NOTES SECTION SHALL BE THROUGHLY CHECKED AND SHOW ONLY RELEVANT NOTES TYP. |  |  |
| 28 | Page 3 | 14 SHEET 1 REFER DESIGN CALCULATION COMMENTS TYP. Noted |  |  |
| 29 | Page 3 | 15 SHEET 1 PROVISIONALLY APPROVED IN CODE-2 ONLY FOR PROGRESS. Noted |  |  |
| 30 | Page 3 | 16 SHEET 2 REFER SHEET-01 COMMENTS Noted |  |  |
| 31 | Page 4 | Duplicated, remove it |  |  |
| 32 | Page 4 | is this note required Typ. |  |  |
| 33 | Page 4 | Provide the layout, location, and specific details for the cable cellar fence and doors. This must include foundations and kerb details for both fence and gate posts, as per the SHAH CDS Substation building cable cellar standards. Additionally, provide the foundation details for the HVAC platform. |  |  |
| 34 | Page 4 | Why this staircase step pedestal height as 300mm try to maintain less than 200mm similar to other step foundation as per standard |  |  |
| 35 | Page 4 | Why this staircase step pedestal is 300mm try to maintain less than 200mm similar to other step foundation Why this staircase step pedestal is 300mm try to maintain less than 200mm similar to other step foundation Why this staircase step pedestal is 300mm try to maintain less than 200mm similar to other step foundation |  |  |
| 36 | Page 4 | Show anchor bolt in pedestal Typ. |  |  |
| 37 | Page 4 | indicate the FGL elevation and reference ADD. |  |  |
| 38 | Page 4 | aS per vendor drawing total height upto baseplate bottom as 1500mm, here 1525mm including grouting, check and correct it |  |  |
| 39 | Page 4 | aS per vendor drawing total height upto baseplate bottom as 1500mm, here 1525mm including grouting, check and correct it. 1475 or 1500, check. |  |  |
| 40 | Page 4 | change the re-bar configuration, main bar to be in longer direction for combined footing. |  |  |
| 41 | Page 4 | Correct the foundation numbers Typ. |  |  |
| 42 | Page 4 | Indicate the anchor bolt type and description as per standard drawing |  |  |
| 43 | Page 4 | The anchor bolt configuration shall be thoroughly verified with respect to the design comments provided in the structural design calculations, ensuring alignment with the considered support conditions. This design drawing must be revised to reflect the final structural design calculations, structural drawings, and foundation input drawings (refer to Company comments). Additionally, ensure the drawing is updated in accordance with the comments provided on the foundation design calculations. |  |  |
| 44 | Page 4 | provide note "Anchor bolt positions and details shall be verified and executed in strict coordination with the relevant structural steel drawings and foundation input drawings. The Contractor is responsible for ensuring alignment between the steel base plates and the concrete foundations prior to casting." |  |  |
| 45 | Page 4 | Why this foundation re-bar only 12-200 try to maintain uniformity. |  |  |
| 46 | Page 4 | Increase the pedestal size to 400*400mm to maintain the minimum required projection beyond the 300mm base plate, in accordance with Company standards. |  |  |
| 47 | Page 5 | Remove Structure drawing related desciption Typ. |  |  |
| 48 | Page 5 | Mention the Anchor bolt description and Type as per anchor bolt standard drawing |  |  |
| 49 | Page 5 | Hilti bolt as per vendor drawing, correct it |  |  |
| 50 | Page 5 | It is the Contractor’s responsibility to conduct a comprehensive check of the drawings. Any errors arising from a failure to coordinate these documents during construction will be the Contractor's liability |  |  |
| 51 | Page 5 | The 300mm footing thickness is inadequate for this lifting lug configuration. Increase the footing thickness to accommodate the minimum straight development length requirements as per ACI standards. |  |  |
| 52 | Page 5 | Refer sheet-01 comments |  |  |

| 1 | SHEET 1 | GRID DIMENSION AND CENTRE LINE DIMENSION OF SUPPORT IS NOT MATCHING WITH VENDOR GA DRAWING TYP. GRID LINE AT THE EDGE OF STEEL COLUMN NO AT THE CENTRELINE OF COLUMN, ALL GRIDS AND DIMENSIONS SHALL BE THROUGHLY CHECKED WITH VENDOR DRAWING AND UPDATED FULLY. | Noted and the drawing is updated as per latest vendor GA |  |
| --- | --- | --- | --- | --- |
| 2 | SHEET 1 | GRID NUMBER NOT MATCHING DIMENSION NOT MATCHING WITH VENDOR GA, CORRECT IT AS PER FINAL DRAWING, CHECK THE NORTH ORIENTATION WITH PSS VENDOR GA DRAWING | ` Noted and the drawing is updated as per latest vendor GA |  |
| 3 | SHEET 1 | IS ONLY THIS LIFTING SLEEVE SUFFICIENT FOR FOUNDATION LIFTING, CHECK WITH DESIGN, TRY TO PROVIDE LIFTING LUG ON FOUNDATION INSTEAD PROVIDING SLEEVE ON PEDESTAL TYP. | Noted and updated in the drawing. |  |
| 4 | SHEET 1 | WATER TABLE SHALL BE CHECKED WITH GEOTECH REPORT, ACCORDINGLY PROVIDE THE CONCRETE PROTECTION AGAINST GROUND WATER PROTECTION TYP. | As per Geotech report, no water table encountered. |  |
| 5 | SHEET 1 | LIFTING LUG TO BE DESIGN VERIFIED TYP. | Noted and presented |  |

| S. No. | Reference / Page No. | COMPANY Comments | CONTRACTOR Response | Status / Remarks |
| --- | --- | --- | --- | --- |

| 6 | SHEET 1 | THIS DRAWING IS PRELIMINARY SUBMISSION WITH AVAILABLE INPUTS, SAME TO BE UPDATED AS PER FINAL VENDOR INPUTS WITH PROPER CHECKING AND WITHOUT ANY DRAFTING ERRORS AND HOLD POINTS TO BE UPDATED IN NEXT REVISION WITH FINAL VENDOR INPUTS. | Noted and submitted based on the latest vendor data |  |
| --- | --- | --- | --- | --- |
| 7 | SHEET 1 | TEXT TO BE IN SAME ALIGNMENT TYP. | Noted and updated |  |
| 8 | SHEET 1 | ALL THE FOUNDATION DIMENSION AND RE-BAR DETAILS, PEDESTAL HEIGHT ARE TO BE VERIFIED AND UPDATED AS PER FINAL VENDOR INPUTS AND MAT 3D DESIGN | Noted and updated |  |
| 9 | SHEET 1 | BOC? | Noted and corrected |  |
| 10 | SHEET 1 | PEDESTAL AND FOUNDATION ORIENTATION SHALL BE AS PER FOUNDATION PLAN TYP. | Noted and updated |  |
| 11 | SHEET 1 | CORRECT THE LEADERS OF FILLS TYP. | Noted and updated |  |

| S. No. | Reference / Page No. | COMPANY Comments | CONTRACTOR Response | Status / Remarks |
| --- | --- | --- | --- | --- |

| 12 | SHEET 1 |  | CHECK THE ANCHOR BOLT SCOPE OF SUPPLY PROVIDE THE ANCHOR BOLT DETAILS, SHOW AS PER ACTUAL ANCHOR BOLT LENGTH TYP. |  | Noted and updated |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 13 | SHEET 1 |  | NOTES SECTION SHALL BE THROUGHLY CHECKED AND SHOW ONLY RELEVANT NOTES TYP. |  | Noted and updated |  |  |
| 14 | SHEET 1 |  | REFER DESIGN CALCULATION COMMENTS TYP. |  | Noted |  |  |
| 15 | SHEET 1 |  | PROVISIONALLY APPROVED IN CODE-2 ONLY FOR PROGRESS. |  | Noted |  |  |
| 16 | SHEET 2 |  | REFER SHEET-01 COMMENTS |  | Noted |  |  |
|  |  | ORIGINATOR |  | REVIEWED BY |  | APPROVED BY |  |
| Name |  | LAVANYA.S |  | KALAI SELVI |  | RAHUL PRAFULLA KHANDEKAR |  |
| Sign |  |  |  |  |  |  |  |
| Date |  | 10/12/2025 |  | 10/12/2025 |  | 10/12/2025 |  |