| S. No. | Reference / Page No. | COMPANY Comments | CONTRACTOR Response | Status / Remarks |
| --- | --- | --- | --- | --- |

| 1 | SHEET 1 | GRID DIMENSION AND CENTRE LINE DIMENSION OF SUPPORT IS NOT MATCHING WITH VENDOR GA DRAWING TYP. GRID LINE AT THE EDGE OF STEEL COLUMN NO AT THE CENTRELINE OF COLUMN, ALL GRIDS AND DIMENSIONS SHALL BE THROUGHLY CHECKED WITH VENDOR DRAWING AND UPDATED FULLY. | Noted and the drawing is updated as per latest vendor GA |  |
| --- | --- | --- | --- | --- |
| 2 | SHEET 1 | GRID NUMBER NOT MATCHING DIMENSION NOT MATCHING WITH VENDOR GA, CORRECT IT AS PER FINAL DRAWING, CHECK THE NORTH ORIENTATION WITH PSS VENDOR GA DRAWING | ` Noted and the drawing is updated as per latest vendor GA |  |
| 3 | SHEET 1 | IS ONLY THIS LIFTING SLEEVE SUFFICIENT FOR FOUNDATION LIFTING, CHECK WITH DESIGN, TRY TO PROVIDE LIFTING LUG ON FOUNDATION INSTEAD PROVIDING SLEEVE ON PEDESTAL TYP. | Noted and updated in the drawing. |  |
| 4 | SHEET 1 | WATER TABLE SHALL BE CHECKED WITH GEOTECH REPORT, ACCORDINGLY PROVIDE THE CONCRETE PROTECTION AGAINST GROUND WATER PROTECTION TYP. | As per Geotech report, no water table encountered. |  |
| 5 | SHEET 1 | LIFTING LUG TO BE DESIGN VERIFIED TYP. | Noted and presented |  |

| S. No. | Reference / Page No. | COMPANY Comments | CONTRACTOR Response | Status / Remarks |
| --- | --- | --- | --- | --- |

| 6 | SHEET 1 | THIS DRAWING IS PRELIMINARY SUBMISSION WITH AVAILABLE INPUTS, SAME TO BE UPDATED AS PER FINAL VENDOR INPUTS WITH PROPER CHECKING AND WITHOUT ANY DRAFTING ERRORS AND HOLD POINTS TO BE UPDATED IN NEXT REVISION WITH FINAL VENDOR INPUTS. | Noted and submitted based on the latest vendor data |  |
| --- | --- | --- | --- | --- |
| 7 | SHEET 1 | TEXT TO BE IN SAME ALIGNMENT TYP. | Noted and updated |  |
| 8 | SHEET 1 | ALL THE FOUNDATION DIMENSION AND RE-BAR DETAILS, PEDESTAL HEIGHT ARE TO BE VERIFIED AND UPDATED AS PER FINAL VENDOR INPUTS AND MAT 3D DESIGN | Noted and updated |  |
| 9 | SHEET 1 | BOC? | Noted and corrected |  |
| 10 | SHEET 1 | PEDESTAL AND FOUNDATION ORIENTATION SHALL BE AS PER FOUNDATION PLAN TYP. | Noted and updated |  |
| 11 | SHEET 1 | CORRECT THE LEADERS OF FILLS TYP. | Noted and updated |  |

| S. No. | Reference / Page No. | COMPANY Comments | CONTRACTOR Response | Status / Remarks |
| --- | --- | --- | --- | --- |

| 12 | SHEET 1 |  | CHECK THE ANCHOR BOLT SCOPE OF SUPPLY PROVIDE THE ANCHOR BOLT DETAILS, SHOW AS PER ACTUAL ANCHOR BOLT LENGTH TYP. |  | Noted and updated |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 13 | SHEET 1 |  | NOTES SECTION SHALL BE THROUGHLY CHECKED AND SHOW ONLY RELEVANT NOTES TYP. |  | Noted and updated |  |  |
| 14 | SHEET 1 |  | REFER DESIGN CALCULATION COMMENTS TYP. |  | Noted |  |  |
| 15 | SHEET 1 |  | PROVISIONALLY APPROVED IN CODE-2 ONLY FOR PROGRESS. |  | Noted |  |  |
| 16 | SHEET 2 |  | REFER SHEET-01 COMMENTS |  | Noted |  |  |
|  |  | ORIGINATOR |  | REVIEWED BY |  | APPROVED BY |  |
| Name |  | LAVANYA.S |  | KALAI SELVI |  | RAHUL PRAFULLA KHANDEKAR |  |
| Sign |  |  |  |  |  |  |  |
| Date |  | 10/12/2025 |  | 10/12/2025 |  | 10/12/2025 |  |